Technical Reference

Unbundled 2-Wire Analog Loop

Technical Specifications

Document History

| Issue No. | Date | Description |
| --- | --- | --- |
| 1 | June 1996 | First working draft; Document released for internal use. |
| 2 | Dec 1996 | Changed leakage requirement; First version of document to be released to the public. |
| 3 | October 1998 | Changed some terminology; Changed CODF Wiring and Tie Cable(s) specification. |
|  | August 2009 | Changed Bell Atlantic logo and references to Verizon |

Copyright © 1998 by Verizon

All Rights Reserved

Printed in U.S.A.

Notice

This Technical Reference is published by Verizon to provide the technical specifications associated with unbundled 2-Wire Analog loops. To the extent feasible, the description references or duplicates existing published technical references utilized by the industry.

Verizon reserves the right to revise this technical reference for any reason including, but not limited to, changes in tariffs, laws, or regulations, conformity with updates and changes in standards promulgated by various agencies, utilization of advances in the state of technical arts, or the reflection of changes in the design of any facilities, equipment, techniques, or procedures described or referred to herein. Liability for difficulties arising from technical limitations or changes herein is disclaimed.

Verizon reserves the right not to offer any or all of these services and to withdraw any or all of them at any future time. In addition, the services described herein are based on available facilities and equipment and may not be universally available.

With respect to services offered pursuant to tariff, however, the terms and conditions of the service offering are determined by the tariff itself and applicable laws and regulations. This reference is intended to be supplemental to the tariffs. In the event of a conflict between the tariffs, laws or regulations and this reference, the tariffs, laws, and regulations shall govern.

For additional copies, please contact:

Verizon Document and Information Delivery Services

1310 N. Court House Road

Arlington, VA 22201

703-974- 5887

For information about the technical specifications in this TR, contact:

Trone Bishop

6E

13100 Columbia Pike

Silver Spring, MD 20904

301-236-3754

Unbundled 2-Wire Analog Loop

Technical Specifications

Contents			Page

1.	General								3

2.	Service Description						4

A.	General							4

B.	Physical Characteristics					4

C.	Service Elements					4

D.	Compatibility Considerations				5

3.	Network Element Specifications					6

A.	General							6

B.	CODF Wiring and Tie Cable(s)				6

C.	Subscriber Loop Facilities				6

D.	Transmission and Signaling (T&S)

Enhancement Equipment				8

4.	Service Specifications						9

5.	CLEC Equipment and CO Cabling Requirements			11

A.	CLEC Equipment Requirements				11

B.	CLEC Equipment CO Cabling Requirements		12

6.	References							13

A.	Definitions						13

B.	Acronyms						16

7.	Bibliography							17

8.	Appendix A: Loop Design Rules					18

Unbundled 2-Wire Analog Loop

Technical Specifications

Figures									Page

Figure 2-1: Typical Unbundled 2WA Loop Configuration			4

Figure 4-1: 2WA Loop Acceptance Limits (AL) and Immediate 		9

Action Limits (IAL)

Figure 4-2:  2WA NC Codes						10

Figure 4-3: Compatible 2WA NCI Code Combinations			10

Figure 4-4: 2WA NCI Code Descriptions					10

Figure 4-5: Compatible TLP Ranges for 2WA Loops			10

1.	General

1.01	This document provides the technical specifications for the unbundled 2-Wire Analog (2WA) loop offered by Verizon in tariffs and contracts.

1.02	This technical reference has been reissued to update some of the terminology. For example, Basic Unbundled Loop Service (BULS) is now known as an unbundled 2WA loop and Other Telephone Companies (OTCs) are now referred to as Certified Local Exchange Carriers (CLECs). In addition, the Central Office Distributing Frame wiring and tie cable specification has been changed and several editorial changes have been made.

1.03	Unbundled 2WA loops enable CLECs that are collocated in a Verizon (VZ) Central Office (CO) to connect to effective 2-wire subscriber loops that support voicegrade analog signals and loop-start signaling.

1.04	The technical specifications in this document assume that the CLEC is collocated in the same CO as the unbundled 2WA loop. In the future, Verizon may offer transport services for unbundled 2WA loops. In such instances, the specifications associated with the transport service should be consulted.

1.05	Unbundled 2WA loops are not represented to support voiceband data (e.g., V.32, V.32bis, V.34, V.PCM, V.90, etc.) transmission. If a customer is able to send and receive data, Verizon will not guarantee a data rate.

2.	Service Description

A.	General

2.01	The description, terms and conditions, rates, regulations, and Universal Service Order Codes (USOCs) for unbundled 2WA loops are contained in applicable tariffs or contracts.

2.02	The unbundled 2WA loop provides the customer with an effective 2-wire transmission channel that is suitable for the transport of loop-start signaling and voicegrade analog signals. The channel is between the Central Office Distributing Frame (CODF) termination of CLEC equipment in a VZ Central Office (CO) and the Network Interface Device (NID) or Rate Demarcation Point (RDP) at an end-user customer location.

2.03	The unbundled 2WA loop is provided subject to availability on a first-come first-served basis. When appropriate facilities are not available, CLECs may avail themselves of VZ construction services.

B.	Physical Characteristics

2.04	The interface of the unbundled 2WA loop at the CODF termination is 2-wire and the interface at the End-User NID or RDP is 2-wire. At each 2-wire interface, one conductor is called tip and the other conductor is called ring. A typical unbundled 2WA loop configuration is shown in Figure 2-1.

CLEC-POT                                                 NID or RDP

Figure 2-1: Typical Unbundled 2WA Loop Configuration

2.05	The transmission channel between the unbundled 2WA loop interfaces is effective 2-wire. An effective 2-wire channel may consist entirely of 2-wire facilities or it may contain a 4-wire facility portion (such as a Digital Loop Carrier) with a 2-wire metallic extension to the end-users NID or RDP. The transmission channel is suitable for the transport of voicegrade analog signals between approximately 300 and 3000 Hz.

2.06	An unbundled 2WA loop may be provided using a variety of loop transmission technologies, including but not limited to, metallic cable, metallic cable based digital loop carrier, and fiber optic digital loop carrier systems.

2.07	When digital loop carrier (DLC) is used to provide an unbundled 2WA loop, the DLC will provide loop-start signaling at the NID or RDP that meets the network requirements in ANSI T1.401-1993 [1].

C.	Service Elements

2.08	An unbundled 2WA loop ordinarily consists of two elements:

(1)	the CODF wire and tie cable(s) between the CODF termination of the collocated CLEC equipment and the CODF termination of a subscriber loop; and,

(2)	a subscriber loop facility between the CODF and the end-user customer's NID or RDP. The loop is either:

(a) a metallic facility consisting of cable and wire between the CODF and the NID or RDP; or,

(b) a universal DLC channel with loop start (LS) signaling capability. The DLC channel consists of:

-	CO cabling between the CODF and a DLC Central Office Terminal 	(COT) 	equipped with a LS open-end channel unit;

-	a fiber or metallic facility from the DLC COT to the DLC Remote Terminal 	(RT) equipped with a LS closed-end channel unit; and,

-	cable and wire between the DLC RT and the NID or RDP.

D.	Compatibility Considerations

2.09	Unbundled 2WA loops utilize subscriber loop facilities that have been designed for Plain Ordinary (analog) Telephone Service (POTS). In most cases, unbundled 2WA loops should be suitable for loop-start single line residential service or loop-start single line business service. POTS qualified loops may not be suitable for data or other special services however.

2.10	Unbundled 2WA loops are not represented to support voiceband data (e.g., V.32, V.32bis, V.34, V.PCM, V.90, etc.) transmission. If a customer is able to send and receive data, Verizon will not guarantee a data rate.

2.11	Special services such as Centrex, Foreign Exchange, Secretarial, and Wide Area Telephone Service lines may have service requirements that are more stringent than POTS. If such services are provided using an unbundled 2WA loop, and electronic transmission and signaling enhancement equipment is required to meet the more stringent requirements, the CLEC will be responsible for providing such enhancement equipment.

2.12	Verizon will work with the CLEC to resolve facility problems should the unbundled 2WA loop require enhancement equipment to support loop-start POTS voice service.

3.	Network Element Specifications

A.	General

3.01	Two network elements are always used with unbundled 2WA loops. They are: CODF wire and tie cable(s), and subscriber loop facilities. Electronic transmission and signaling enhancement equipment, is used rarely with unbundled 2WA loops however it has been included here for completeness. The sections which follow contain the specifications for each of these network elements.

B.	CODF Wiring and Tie Cable(s)

3.02	CODF cross-connect wiring and tie cable(s) are used to link the CODF termination of collocated CLEC equipment to the CODF termination of metallic subscriber loops, DLC COTs, and in rare instances, electronic transmission and signaling enhancement equipment.

3.03	The total combined length of all CODF cross-connect wiring and all CODF-to-CODF tie cables between the CODF termination of the CLEC equipment and the CODF termination of any subscriber loop in the same CO should be less than 1500 feet.

3.04	The direct-current resistance between the CODF termination of the CLEC equipment and the CODF termination of any subscriber loop in the same CO should be less than 125 ohms. This is equal to 1500 or less feet of 26 gauge cable.

3.05	The 1kHz loss measured on the CODF wiring and tie cables when measured between 900 ohm impedances should be .8 dB or less.

3.06	The C-message noise measured on the CODF wiring and tie cables shall be 20 dBrnC or less.

C.	Subscriber Loop Facilities

3.07	Subscriber loop facilities consist of feeder and distribution plant between the CODF and the end-user customer's NID or RDP. Feeder plant uses a variety of transmission technologies, including but not limited to, twisted-pair metallic cables, twisted-pair metallic cable based digital loop carrier, and fiber optic based digital loop carrier. Distribution plant usually consists of multipair metallic cables. Additional information about subscriber loops may be found in Bellcore SR-2275 [2] and appendix A of this document.

3.08	A twisted-pair metallic loop facility consists entirely of  metallic cable and wire between the CODF and the end-user customer's NID or RDP. Most metallic loops consist of multipair cables, laid out on aerial, underground, or buried routes to suit the needs of a particular community. The metallic loop facility may be loaded or non-loaded. It may also have bridged tap however loaded bridged tap and bridged tap between load coils are not permitted.

3.09	A universal DLC facility consists of CO cabling between the CODF and a DLC COT, OSP fiber or metallic cable facilities from the DLC COT to the DLC RT, and multi-pair cable and drop wire between the DLC RT and the end-user customer's NID or RDP. Some DLC may not support enhanced services such as distinctive ringing, forward disconnect, caller ID, etc.

3.10	Subscriber loop facilities have been designed on a global basis primarily to accommodate POTS and guarantee that loop transmission loss is statistically distributed and that no single loop exceeds the signaling range of the CO.

3.11	Prior to 1980, loops were designed using one of the following design plans: Resistance Design (RD), Long Route Design (LRD), or Unigauge Design (UD). From 1980 to 1986, the Modified Resistance Design (MRD), Modified Long Route Design (MLRD), and Concentrated Range Extension with Gain (CREG) plans were applied on a going-forward basis (i.e., retroactive redesign was not implemented). In 1986, the Revised Resistance Design (RRD) plan was applied on a going-forward basis. Appendix A provides a summary of the various loop design plans.

3.12	Most metallic loop facilities (98%) were designed using the RD, MRD, or RRD design rules. The RRD design rules currently in use limit the loop resistance to the design range of the CO switch (1300 or 1500 ohms) or 1500 ohms whichever is less. The 1 kHz loss of RRD loops is 8.5 dB or less.

3.13	A small number of loops have been designed using the LRD, MLRD, UD, and CREG design plans. These loops are long (15+kft) and have high resistance (up to 2800 or 3600 ohms) and high loss (up to 13 dB without gain). Such loops require electronic transmission and signaling range enhancement equipment to accommodate POTS. The LRD and MLRD design plans use Range Extension with Gain (REG) equipment that is either dedicated to each loop or hard-wired to the VZ CO line equipment. In the latter case, the hard-wired REG is not available for use with 2WA unbundled loop services.

3.14	The REG equipment used with CREG designed loops is implemented behind a stage of switching concentration in the associated CO switch. This permits REG equipment to be shared with other loops working out of the same CO switch. For this reason, the REG associated with CREG designed loops is not available for use with 2WA unbundled loop services. Verizon will work with the CLEC to explore available options when an LRD, MLRD, or CREG designed loop requires enhancement to support an unbundled 2WA loop.

3.15	The direct-current resistance of a metallic loop facility measured between the CODF and the NID or RDP shall be 1520 ohms or less if the facility was designed using RD, MRD, or RRD rules. The resistance will be 2500 ohms or less if the facility was designed using UD rules, 2800 ohms or less if the facility was designed using CREG or MLRD rules, and 3600 ohms or less if the facility was designed using LRD rules.

3.16	The 1kHz loss of a metallic loop facility when measured with a 900 ohm impedance at the CODF and a 600 ohm impedance at the NID or RDP shall be 8.5 dB or less if the loop was designed using RD, MRD, or RRD rules. The loss will be 10 dB or less if the loop was designed using LRD or MLRD rules, and 13 dB or less if the loop was designed using UD or CREG rules.

3.17	The C-message noise measured on a metallic subscriber loop at the NID or RDP shall be less than 30 dBrnC.

3.18	The insulation resistance or leakage resistance between the tip conductor and ground, the ring conductor and ground, and the tip and ring conductors of a loop shall each be greater than 100 K ohms.

3.19	The longitudinal noise or power influence (PI) measured per IEEE Std 743-1995 [3] on the metallic portion of a loop should be less than 90 dBrnC.

3.20	The longitudinal balance of a metallic subscriber loop is defined as the longitudinal noise (in 	dBrnC) minus the C-message noise (in dBrnC). The longitudinal balance shall be >50 dB.

3.21	DLC facilities shall provide a battery feed to the NID or RDP. When the NID or RDP is terminated by a direct-current resistance of 430 ohms or less, the loop current shall be 20 mA or greater.

3.22	The 1kHz loss of a DLC facility when measured with a 900 ohm impedance at the CODF and a 600 ohm impedance at the NID or RDP shall be 8 dB or less.

3.23	The C-message noise measured on a DLC facility shall be 23 dBrnC or less.

3.24	The C-Notched noise measured on a DLC facility shall be 36 dBrnC or less with a -13 dBm0 1004 Hz holding tone.

3.25	The impulse noise measured on a DLC facility shall be no more than 15 counts in 15 minutes with a threshold of 59 dBrnC.

3.26	The echo return loss and singing return loss of a subscriber loop facility measured with a 900 ohm + 2.16 (f reference at the CODF and a 600 ohm + 2.16 (f termination at the NID or RDP shall be equal to or greater than 5.5 dB and 2.5 dB respectively.

3.27	Subscriber loop facilities shall meet all applicable design specifications. (See appendix A)

D.	Transmission and Signaling (T&S) Enhancement Equipment

3.28	Transmission and signaling (T&S) enhancement equipment is sometimes used with unbundled 2WA loops. Several different types of T&S equipment can be used. Examples are: transmission repeaters; loop signaling repeaters;  and signaling battery boost equipment.

3.29	T&S equipment is often used with unbundled 2WA loops designed to LRD, MLRD, UD, and CREG rules. Such devices are often called Range Extenders with Gain (REGs).

3.30	The impedance of T&S equipment shall be a nominal 900 ohms when used in the CO and a nominal 600 ohms when used at or near the NID or RDP.

3.31	T&S equipment shall provide 20 mA or more of loop current when the NID or RDP is terminated by a direct-current resistance of 430 ohms or less.

3.32	The C-message noise measured on T&S equipment shall be 20 dBrnC or less.

3.33	The C-Notched noise measured on T&S equipment shall be 36 dBrnC or less with a -13 dBm0 1004 Hz holding tone.

4.	Service Specifications

4.01	The overall end-to-end unbundled 2WA loop service is from the CODF termination of the CLEC equipment  to the end-user customer's NID or RDP.

4.02	2WA loop parameters are tested at the NID or RDP in response to trouble reports or when additional testing is purchased.

4.03	Acceptance Limits (AL) and Immediate Action Limits (IAL) are shown in Figure 4-1 for loops designed to RD, MRD, and RRD rules. The resistance and loss parameters of loops designed to LRD, MLRD, UD, and CREG rules are in Appendix A.

Figure 4-1:  2WA Loop Acceptance Limits (AL) and Immediate Action Limits (IAL)

| PARAMETER | AL | IAL |
| --- | --- | --- |
| 1004 Hz Loss | < 8.5 dB | > 10.0 dB |
| Resistance | < 1520 ohms | > 1520 ohms |
| Insulation Resistance | > 100 k ohms | < 100 k ohms |
| C-Message Noise | < 30 dBrnC | > 30 dBrnC |
| Power Influence (Noise to Ground) | < 90 dBrnC | > 90 dBrnC |
| Loop Current (DLC only) | > 20 mA | < 20 mA |

4.04	2WA loops shall meet the loop-start requirements in ANSI T1.401-1993 [1].

4.05	2WA loops are not represented to support voiceband data (e.g., V.32, V.32bis, V.34, V.PCM, V.90 etc.) transmission. If a customer is able to send and receive data, Verizon will not guarantee a data rate.

4.06	The Network Channel (NC) codes and Network Channel Interface (NCI) codes associated with 2WA loops are shown in the following figures: Figure 4-2 shows NC codes; Figure 4-3 shows compatible NCI code combinations; Figure 4-4 shows NCI code descriptions; and Figure 4-5 shows compatible TLP ranges.

Figure 4-2:  2WA NC Codes

| NC Code | Character 3 | Character 4 |
| --- | --- | --- |
| LX | - | - |

Figure 4-3: Compatible 2WA NCI Code Combinations

| CLEC-POT | EU-POT |
| --- | --- |
| 02QC3.OOD | 02LS2 |

Figure 4-4: 2WA NCI Code Descriptions

| NCI Code | Description |
| --- | --- |
| 02LS2 | 2-Wire Loop-start signaling - Closed End - 600 ohms |
| 02QC3.OOD | 2-Wire Loop-start signaling - Open End - 900 ohms |

Figure 4-5: Compatible TLP Ranges for 2WA Loops

| EU/CLEC Transmit TLP | EU/CLEC Receive TLP |
| --- | --- |
| 0 | 0 to -10.0 (1) |

(1) In general, the receive TLP is a function of the cable loss.

5.	CLEC Equipment and CO Cabling Requirements

A.	CLEC Equipment Requirements

5.01	Collocated CLEC equipment used for interconnection with unbundled 2WA loops shall meet all of the applicable generic equipment requirements in Bellcore GR-63-CORE [4] and Bellcore GR-1089-CORE [5].

5.02	Collocated CLEC equipment used for interconnection with unbundled 2WA loops shall be manufactured in accordance with FCC, NEC, UL, and USDL requirements and orders applicable to Federal, State, and local requirements including, but not limited to, statutes, rules, regulations, orders, or ordinances, or otherwise imposed by law. Requirements that are not specified in this document, contractual technical requirements, or other applicable documents, shall meet the manufacturer's requirements consistent with industry standards.

5.03	The open circuit tip-to-ring dc voltage that collocated CLEC equipment applies to VZ VF cabling shall be less than 80 Vdc.

5.04	Collocated CLEC equipment shall not deliver more than 2.5 watts of power to any load via VZ VF cable.

5.05	Collocated CLEC equipment shall not deliver more than 150 mA of loop current to any load via VZ VF cable.

5.06	The noise limits for unbundled 2WA loops require collocated CLEC equipment to have a longitudinal balance of >60 dB.

5.07	The loss and noise limits for 2WA unbundled loop services require collocated CLEC equipment to have a nominal 	impedance of 900 ohms.

5.08	The applied power level of any transmitted signal on an unbundled 2WA loop when averaged over 3 seconds shall not exceed -13 dBm0.

5.09	Loops may be exposed to electrical surges from lightning and commercial power system disturbances. Despite protective devices on the CODF, some of these disturbances are likely to reach CLEC equipment. CLEC equipment shall be designed to withstand certain surges without being damaged, and shall fail in a safe manner under infrequent high stress.

5.10	The prevalent voltage-limiting device available for CO use is the 3-mil carbon block. This device has an upper 3( limiting voltage of 1000 volts peak under surge conditions and 600 volts rms (800 peak) at 60 Hz. CLEC equipment connected to unbundled 2WA loops protected by carbon blocks may be subjected to voltages up to these levels. Unexposed COs may not have primary protection, and CLEC equipment not co-ordinating with carbon blocks may need protection in these locations.

5.11	If the subscriber loop facility is exposed to commercial ac power, the CO protector may also include 350 mA heat coils for limiting the current that is permitted to flow to CO equipment. In addition, a protective fuse cable located outside the CO incorporating 24 or 26 AWG conductors to coordinate with the protector, serves to limit current to safe levels in the event of prolonged operation of the protector during power fault conditions.

B.	CLEC Equipment CO Cabling Requirements

5.12	The voice grade CO cabling used to terminate CLEC equipment on the CODF shall use twisted-pair conductors.

5.13	The type, gauge, and length of the CLEC CODF cabling shall be specified based on this specification and CLEC equipment requirements. If the specifications in this document differ from the CLEC equipment manufacturers specifications, then the more stringent of the two shall be used.

5.14	The direct-current resistance of the CO cabling between the CLEC equipment and the CODF shall meet the CO cabling requirements in the Bellcore FR-64 [6] (i.e., 23 ohms or less). This is equivalent to 275 feet or less of 26 gauge cable, 440 feet or less of 24 gauge cable, and 700 feet or less of 22 gauge cable.

5.15	All CO cabling between CLEC equipment and the CODF shall be equipped with connectors at each end. The type of connectors shall be specified by the VZ CO Engineer.

5.16	The 1kHz loss of the CO cabling between the CLEC equipment and the CODF, when measured between 900 ohm impedances, shall be less than .15 dB.

5.17	The C-message noise measured on the CO cabling between the CLEC equipment and the CODF shall be 20 dBrnC or less.

6.	References

A.	Definitions

Basic Link

The former name for the unbundled 2-wire analog loop service in New York and New England.

Basic Unbundled Loop Service (BULS)

The former name for the unbundled 2-wire analog loop service in the District of Columbia, Delaware, Maryland, New Jersey, Pennsylvania, Virginia, and West Virginia.

Battery Boost

A series aiding battery source that extends the signaling range of current sensing equipment.

Bridged tap

Any branch section of a cable pair, or any extension of a cable pair beyond the point where it is used, in which no direct current flows when customer equipment is connected and used.

Central Office (CO)

A telephone company building which houses equipment and facilities used to provide switched access services.

Central Office Distributing Frame (CODF)

Framework located in a CO that holds wire cross-connects which are used to interconnect cable terminations for end-user customer loops, switching system ports, and inter-office facilities.

Certified Local Exchange Carrier (CLEC)

An organization that has been certified in a state to provide local exchange telecommunications services to the public.

C-Message Noise

The frequency-weighted, short-term average noise within an idle channel. The frequency weighting, called C-message, is used to account for the variations in 500-type telephone set transducer efficiency and end-user annoyance to tones as a function of frequency.

C-Notched Noise

The C-message frequency-weighted noise on a channel with a holding tone that is removed at the measuring end through a notch (very narrow band) filter.

Channel

An electrical, or photonic communications path between two or more points of transmission.

Closed End

The end of a switched access service that receives ringing and dial tone and transmits address signals.

dBm

A unit for expression of power level in decibels relative to one milliwatt.

dBm0

A unit used to express power level in decibels relative to one milliwatt referred to, or measured at, a zero transmission level point (0TLP).

dBrn

A unit used to express noise power in decibels relative to one picowatt (-90 dBm).

dBrnC

A unit used to express noise power in decibels relative to one picowatt measured with C-message weighting.

dBrnC0

Noise power in dBrnC referred to, or measured at, a zero transmission level point (0TLP).

Decibel (dB)

The logarithmic unit of signal power ratio most commonly used in telephony. It is used to express the relationship between two signal powers, usually between two acoustic, electric, or optical signals; it is equal to ten times the common logarithm of the ratio of the two signal powers.

Facilities

Any cable, poles, conduit, microwave, or carrier equipment, central office distributing frames, central office switching equipment, computers (both hardware and software), business machines, etc., utilized to provide the services offered by a telephone company.

Impulse Noise

Any momentary occurrence of noise on a channel that significantly exceeds the normal noise peaks. Impulse noise is analyzed by counting the number of occurrences that exceed a threshold.

Insulation Resistance (Leakage Resistance)

The resistance between the conductors of an insulated metallic pair or the resistance between each conductor of an insulated metallic pair and ground.

Loop

A transmission channel between a end-user customer location and a VZ CO that is used as a transmission channel for telephone company services.

Loop-start (LS) Signaling

A type of switched access line signaling in which the network provides a battery source. To initiate a call, customer premises equipment will provide a loop closure that causes dc loop current to flow which the network will detect.

Open End

The end of a switched access service that transmits ringing and dial tone and receives address signaling.

Plain Ordinary Telephone Service (POTS)

The basic single line switched access service offered by local exchange carriers to residential and business customers. POTS uses loop-start signaling.

Power Influence (PI)

The power of an unwanted longitudinal signal that is induced onto a metallic loop by an electromagnetic field emanating from a conductor or conductors of a power system. PI is also called longitudinal noise or noise to ground.

Rate Demarcation Point (RDP)

The point at which Verizon network access recurring charges and responsibility stop and beyond which customer responsibility begins. The RDP is the point of demarcation and/or interconnection between a Verizon subscriber loop facility and end-user premises cabling or terminal equipment. Verizon facilities at, or constituting, the rate demarcation point shall consist of wire or a jack conforming to Subpart F of Part 68 of FCC rules.

Signaling Repeater

Loop enhancement equipment that detects and regenerates signaling states.

Transmission Repeater

Loop enhancement equipment that amplifies and equalizes voice frequency signals.

Unbundled 2WA Loop

An effective 2-wire transmission channel between a end-user customer location and a LEC CO that is not a part of, or connected to, other LEC services. An unbundled 2WA loop is suitable for the transport of voicegrade analog signals and loop start signaling. In the past, the unbundled 2WA loop was known as Basic Unbundled Loop Service (BULS) and Basic Link.

Voicegrade (VG)

A term used to describe a channel, circuit, facility, or service that is suitable for the transmission of speech, digital or analog data, or facsimile, generally with a frequency range of about 300 to 3000 Hz.

B.	Acronyms

ANSI			American National Standards Institute

BULS			Basic Unbundled Loop Service

CLEC			Certified Local Exchange Carrier

CLEC-POT		Certified Local Exchange Carrier - Point Of Termination

CO			Central Office

CODF			Central Office Distributing Frame

COT			Central Office Terminal

CREG			Concentrated Range Extension with Gain

DLC			Digital Loop Carrier

EU			End User

EU-POT		End User Point Of Termination

FCC			Federal Communications Commission

GS			Ground-Start

IEEE			International Electrical and Electronic Engineers

LRD			Long Route Design

LS			Loop-Start

MLRD			Modified Long Route Design

MRD			Modified Resistance Design

NEC			National Electric Code

NID			Network Interface Device

PI			Power Influence

POTS			Plain Ordinary Telephone Service

RD			Resistance Design

RDP			Rate Demarcation Point

REG			Range Extender with Gain

RRD			Revised Resistance Design

RT			Remote Terminal

T&S			Transmission and Signaling

UD			Unigauge Design

UL			Underwriter's Laboratory

USDL			United States Department of Labor

VF			Voice Frequency

VG			Voicegrade

VZ			Verizon

2WA 			2-Wire Analog

7.	Bibliography

1-	ANSI T1.401-1993, American National Standard for Telecommunications - Interface Between Carriers and Customer Installations - Analog Voicegrade Switched Access Lines Using Loop-Start and Ground-Start Signaling.

2-	Special Report SR-2275, Issue 3, Bellcore Notes on the Networks; Bellcore; December 1997.

3-	ANSI/IEEE 743-1995, Standard Methods and Equipment for Measuring the Transmission Characteristics of Analog Voice Frequency Circuits.1

4-	Generic Requirements GR-63-CORE, Issue 1, Network Equipment-Building System (NEBS) Requirements: Physical Protection; Bellcore; October 1995. 2

5-	Generic Requirements GR-1089-CORE, Issue 2, Electromagnetic Compatibility and Electrical 		Safety - Generic Criteria for Network Telecommunications Equipment; Bellcore; December 			1997. 2

6-	Family of Requirements FR-64, LATA Switching Systems Generic Requirements (LSSGR) 1998 Edition; Bellcore; February 1998. 2

NOTE: These documents are subject to change. References reflect the most current information available at the time of printing. Readers are advised to check the status and availability of all documents.

Appendix A: Loop Design Rules

1-	Resistance Design (RD): (96% of loops designed prior to 1980)

0 - 1300 ohms, 8.5 dB max

Max BT on NL cable = 6 kft

POTS = No loading to 18 kft, H88 loading beyond 18 kft

PBX and CENTREX = No loading to 9 kft, H88 loading beyond 9 kft

Max end section plus BT = 15 kft

No loaded BT, No BT between load coils.

2-	Long Route Design (LRD): (3% of loops designed prior to 1980)

1301 - 3600 ohms, 10 dB max

Applicable > 18 kft, full H88 loading

Gain required for loops over 1600 ohms

Max end section plus BT = 12 kft

No loaded BT, No BT between load coils.

3-	Unigauge Design (UD): (1% of loops designed prior to 1980)

0 - 2500 ohms, 13 dB max

No loading to 24 kft, partial H88 loading beyond 24 kft

Gain applied to loops > 15 kft

Max BT on NL cable = 6 kft

End section plus BT = 12 kft

No loaded BT, No BT between load coils.

4-	Modified Resistance Design (MRD): (1980 - 1986)

0 - 1500 ohms, 8.5 dB max

Max BT on NL cable = 6 kft

Total NL cable plus BT = 15 kft

POTS = No loading to 15 kft, full H88 loading beyond 15 kft

PBX and CENTREX = No loading to 9 kft, H88 loading beyond 9 kft

Loaded cable end section plus BT = 3 to 12 kft

No loaded BT, No BT between load coils.

5-	Modified Long Route Design (MLRD): (1980 - 1986)

1501 - 2000 ohms = Res Zone 18

2001 - 2800 ohms = Res Zone 28

RZ 18 = Range Extension plus 3 dB of gain, 10 dB max

RZ 28 = Range Extension plus 6 dB of gain, 10 dB max

Full H88 loading

End section plus BT = 3 to 12 kft

No loaded BT, No BT between load coils.

6-	Concentrated Range Extension with Gain (CREG): (1980 - 1986, 1A & 2A ESS Only)

0 - 2800 ohms, 13 dB max

No loading to 15 kft, full H88 loading beyond 15 kft

Range extension with gain (REG) required for all loops over 1500 ohms

REG provided behind a stage of switching concentration

Total NL cable plus BT = 15 kft max

Max NL cable BT = 6 kft

Loaded end section plus BT = 3 to 12 kft

No loaded BT, No BT between load coils.

7-	Revised Resistance Design: (after 1986)

0 - 18 kft = 1300 ohms max

18 - 24 kft = 1500 ohms max (CO permitting)

No loading to 18 kft, full H88 loading between 18 - 24 kft

Max NL cable plus BT = 18 kft

Max BT on NL cable = 6 kft

Loaded cable end section plus BT = 3 to 12 kft

No loaded BT, No BT between load coils.

# Footnotes

Ground-start signaling may also be available in some jurisdictions.

Ground-start signaling may be available in some jurisdictions.

Ground-start signaling may be available in some jurisdictions.

If ground-start signaling is offered, it shall meet the ground-start requirements in T1.401-1993 [1].

For ground-start signaling, the CLEC-POT NCI code would be 02QC3.OOB and the EU-POT NCI code would be 02GS2.

In ground-start signaling applications, the CLEC-POT NCI code 02QC3.OOB is defined as 2-wire ground-start signaling - open end - 900 ohms and the EU-POT NCI code 02GS2 is defined as 2-wire ground-start - closed end - 600 ohms.

To obtain ANSI documents, contact American National Standards Institute, Inc., 1430 Broadway, New York, NY 10018.

To obtain Bellcore documents, contact Bellcore Customer Service, 8 Corporate Place - PYA 3A-184, Piscataway, NJ 08854-4156. In the US and Canada, call 1-800-521-CORE. All others call 908-699-5800.

# Text boxes

TR 72565, Issue 3